## Software
SS0075
Fahrenheit / Celsius
GPC-XP Controller
Customer |  |  |  |  | P.O. #
Project |  |  |  |  | Order #
Date
Programmed By: |  |  | Version 1.32 |  |  | Checksum: 0xFB79B1F8
Hardware - OE338-23-GPC XP/YS102432 |  |  |  |  | Pic-Kit -3
Quantity
|  | Processor | PIC32MX695F512L |  |  | 2
|  | BootLoader | SSB00501 v2.04
Device Info
|  | INT LEN | 4BA20
|  | INT SUM | 50F3F218
|  | EEPROM | 27C128 | ID24C128 |  | 1
|  | DRIVER | RS-485 | ID001785 |  | 1
CommLink
Use standard SS0073 software to flash the built in CommLink
Notes | Be sure to program both the GPC controller and the built in CommLink
NOTE: The last digit of the Checksum is irrelevant if using a PICit3
to program this device. Only the first 7 digits are important.
v1.00 - First release of GPC-XP Controller
v1.01 - Fixed Outdoor Air selection. Updated to XC32 compiled bootloader and app code.
v1.02 - Fixed calibration offset for communicating temperature sensors
v1.03 - Fixed Outdoor Air so it could be used as a control input selection.
v1.04 - Customer requested feature added for Rogue Sensor detection on AVC function.
v1.05 - Fixed RTC broadcast from preventing GA() and GB() broadcasts
v1.06 - Fixed Ebus baudrate that was broke last version due to BonLin updates from Po.
v1.07 - Changed AVC values to use programmable decimal point instead of fixed xx.x format
Includes new updated BonLib that fixes zero length comm packets
Include new SSB501 v2.13 bootloader that fixes zero length comm packets
v1.08 - Fixed Schedule Force Off command and added Exception Handler for Watchdog
v1.09 - Fixed Relay Setpoint Reset routine from resetting without a reset source defined.
v1.10 - Fixed Relay Outputs to allow N/O use instead of just N/C use.
v1.11 - Added binary input alarms to main alarm indicator
v1.12 - Fixed negative setpoints for use on Analog Outputs
v1.13 - New feature to broadcast Emergency Shutfdown or Fan Only Operation to VCBX
v1.14 - Fixed AND source divisor to look at correct scaling
v1.15 - Fixed setpoint issue with Logical OR condition statements.
v1.16 - Fixed Analog Outputs broke by updates to BonLib from Po.
v1.17 - Added code to clear PID values when output goes disabled.
v1.18 - Fixed Analog Output Alternate override when using another Analog Output as Alternate Mode
v1.19 - Shortened time it takes to cancel pushbutton override with a long button press
Fixed the temperature sensor from reading temperature while pushbutton is pressed
v1.20 - Fixed factory reset of defaults without the need to power cycle the board
Added new feature for relay to follow any alarm condition
v1.21 - Fixed alternate override for analog inputs being off by one position.
v1.22 - Fixed Sensor Calibration from being affected by Averaging Constant
v1.23 - Changed broadcast state machine to prevent locking into a state and never changing
v1.24 - Fixed more alternate override values being off by one position
v1.25 - Cleared lead/lag alarms when no call to run, so lead would restart if it stopped in alarm mode.
v1.26 - Fixed decimal point location on analog output trendlogs.
v1.27 - Added EBUS LED operation. No affect on any control.
v1.28 - Fixed 4-20 ma readings from inaccuracy.
v1.29 - Fixed Logical AND/OR source controls to accept analog outputs as control source.
Fixed EBUS LED to operate during production test mode.
v1.30 - Resolved hidden warning messages. Updated bootloader to v2.04
v1.31 - Fixed Lead/Lag AND condition tests
v1.32 10/6/23 - Added support for ADS8201 ADC chip.
Form Rev 10/6/23 | [6 empty] | SS0075.XLS